## MOP_E
Report for previous day | [5 empty] | Date of Reporting: |  | 16-Sep-2024
A. Power Supply Position at All India and Regional level
|  | NR | WR | SR | ER | NER | TOTAL
Demand Met during Evening Peak hrs(MW) (at 20:00 hrs; from RLDCs) |  | 66832 | 56266 | 43901 | 21621 | 3318 | 191938
Peak Shortage (MW) |  | 0 | 0 | 0 | 0 | 0 | 0
Energy Met (MU) |  | 1456 | 1341.8 | 1180.18 | 468.45 | 67.53 | 4514.08
Hydro Gen (MU) |  | 363.79 | 106.87 | 160.8 | 95.15 | 29.37 | 755.96
Wind Gen (MU) |  | 20.38 | 115.36 | 200.65 | - | - | 336.39
Solar Gen (MU)* |  | 167.68 | 88.29 | 138.11 | 2.22 | 0.96 | 397.26
Energy Shortage (MU) |  | 0 | 0 | 0 | 0 | 0 | 0
Maximum Demand Met During the Day (MW) (From NLDC SCADA) |  | 67521 | 58727 | 56003 | 21931 | 3333 | 196192
Time Of Maximum Demand Met |  | 19:41 | 19:01 | 10:54 | 00:09 | 21:19 | 10:54
B. Frequency Profile (%)
Region | FVI | < 49.7 | 49.7 - 49.8 | 49.8 - 49.9 | < 49.9 | 49.9 - 50.05 | > 50.05
All India | 0.074 | 0 | 0 | 1.28 | 1.28 | 74.4 | 24.31
C. Power Supply Position in States
|  | Max.Demand | Shortage during | Energy Met | Drawal | OD(+)/UD(-) | Max OD | Energy
Region | States | Met during the day (MW) | maximum Demand (MW) | (MU) | Schedule (MU) | (MU) | (MW) | Shortage (MU)
| Punjab | 13505 | 0 | 306.78 | 189.52 | 0.43 | 734 | 0
| Haryana | 8296 | 0 | 183.25 | 134.98 | -3.75 | 272 | 0
| Rajasthan | 12676 | 0 | 287.28 | 84.87 | 0.96 | 519 | 0
| Delhi | 4630 | 0 | 99.61 | 95.63 | 1.51 | 302 | 0
NR | UP | 23051 | 0 | 446.46 | 212.61 | -2.35 | 507 | 0
| Uttarakhand | 1918 | 0 | 39.97 | 16.86 | -0.93 | 135 | 0
| HP | 1547 | 0 | 31.83 | -3.49 | -1.77 | 94 | 0
| J&K(UT) & Ladakh(UT) | 2521 | 0 | 51.73 | 30.1 | 1.11 | 211 | 0
| Chandigarh | 225 | 0 | 4.71 | 5.25 | -0.54 | 37 | 0
| Railways_NR ISTS | 208 | 0 | 4.5 | 3.95 | 0.55 | 44 | 0
| Chhattisgarh | 5139 | 0 | 119.2 | 67.7 | -1.4 | 233 | 0
| Gujarat | 18759 | 0 | 404.7 | 175.4 | 2.3 | 1197 | 0
| MP | 11129 | 0 | 235.6 | 110.1 | -3.9 | 222 | 0
WR | Maharashtra | 22591 | 0 | 508.3 | 167.2 | 10 | 2175 | 0
| Goa | 615 | 0 | 13.5 | 10.6 | 2.7 | 106 | 0
| DNHDDPDCL | 1265 | 0 | 29.3 | 29.1 | 0.2 | 64 | 0
| AMNSIL | 825 | 0 | 18.5 | 8.8 | 0.6 | 63 | 0
| BALCO | 530 | 0 | 12.7 | 12.6 | 0.1 | 6 | 0
| Andhra Pradesh | 11264 | 0 | 230.91 | 60.2 | 0.32 | 1046 | 0
| Telangana | 13938 | 0 | 274.28 | 129.94 | 3.55 | 2014 | 0
SR | Karnataka | 13304 | 0 | 229.56 | 76.92 | 4.01 | 1663 | 0
| Kerala | 3663 | 0 | 72.54 | 46.39 | 0.41 | 586 | 0
| Tamil Nadu | 16620 | 0 | 362.2 | 147.72 | -8.08 | 1029 | 0
| Puducherry | 470 | 0 | 10.69 | 10.4 | -0.3 | 25 | 0
| Bihar | 6074 | 0 | 125.69 | 118.15 | -3.31 | 118 | 0
| DVC | 2986 | 0 | 64.22 | -30.34 | 0.39 | 362 | 0
| Jharkhand | 1791 | 0 | 26.75 | 22.44 | -5.55 | 269 | 0
ER | Odisha | 5221 | 0 | 106.87 | 29.62 | -2.72 | 499 | 0
| West Bengal | 6842 | 0 | 143.82 | 44.82 | -2.13 | 281 | 0
| Sikkim | 62 | 0 | 0.97 | 1.22 | -0.25 | 7 | 0
| Railways_ER ISTS | 16 | 0 | 0.13 | 0.14 | -0.01 | 4 | 0
| Arunachal Pradesh | 158 | 0 | 3.17 | 2.78 | 0.05 | 21 | 0
| Assam | 2420 | 0 | 46.71 | 38.4 | 0.85 | 168 | 0
| Manipur | 192 | 0 | 2.63 | 2.8 | -0.17 | 22 | 0
NER | Meghalaya | 267 | 0 | 4.57 | 1.56 | -0.13 | 71 | 0
| Mizoram | 106 | 0 | 2.13 | 0.55 | -0.21 | 4 | 0
| Nagaland | 166 | 0 | 3.13 | 2.71 | -0.02 | 22 | 0
| Tripura | 240 | 0 | 5.19 | 4.14 | 0.27 | 8 | 0
D. Transnational Exchanges (MU) - Import(+ve)/Export(-ve)
|  | Bhutan | Nepal | Bangladesh | Godda -> Bangladesh
Actual (MU) |  | 42.66 | 17.21 | -16.673 | -21.8
Day Peak (MW) |  | 1937.59 | 844.656 | -983 | -1131.32
E. Import/Export by Regions (in MU) - Import(+ve)/Export(-ve); OD(+)/UD(-)
|  | NR | WR | SR | ER | NER | TOTAL
Schedule(MU) |  | 245.31 | -186.49 | 107.49 | -172.92 | 6.61 | 0
Actual(MU) |  | 234.38 | -163.83 | 95.385 | -177.14 | 6.24 | -4.965 |  | -10.93
O/D/U/D(MU) |  | -10.93 | 22.66 | -12.105 | -4.22 | -0.37 | -5
F. Generation Outage(MW)
|  | NR | WR | SR | ER | NER | TOTAL | % Share
Central Sector |  | 4979.04 | 14608.9 | 6108 | 3326 | 280 | 29301.94 | 46.4043
State Sector |  | 5595.5 | 13791.5 | 10992 | 3309 | 154.97 | 33842.97 | 53.5957
Total |  | 10574.54 | 28400.4 | 17100 | 6635 | 434.97 | 63144.91 | 100
G. Sourcewise generation (Gross) (MU)
|  | NR | WR | SR | ER | NER | All India | % Share
Coal |  | 684.58 | 1187.86 | 486.57 | 601.14 | 12.78 | 2972.93 | 61.6183
Lignite |  | 25.04 | 11.69 | 56.55 | 0 | 0 | 93.28 | 1.9334
Hydro |  | 363.79 | 106.87 | 160.8 | 95.15 | 29.37 | 755.96 | 15.6039
Nuclear |  | 29.9 | 67.94 | 75.1 | 0 | 0 | 172.94 | 3.5844
Gas, Naptha & Diesel |  | 1.81 | 27.6 | 4.8 | 0 | 22.67 | 56.88 | 1.1789
RES (Wind, Solar, Biomass & Others) |  | 193.58 | 207.14 | 369.46 | 4.73 | 0.96 | 775.83 | 16.081
Total |  | 1298.7 | 1609.1 | 1153.28 | 701.02 | 65.78 | 4827.83 | 100
Share of RES in total generation (%) |  | 14.9057 | 12.873 | 32.0356 | 0.67473 | 1.5323 | 16.081
Share of Non-fossil fuel (Hydro,Nuclear and RES) in total generation(%) |  | 45.2198 | 23.7369 | 52.4903 | 14.2478 | 46.11 | 35.2694
H. All India Demand Diversity Factor |  |  |  | I. All India Peak Demand and shortage at Solar and Non-Solar Hour
Based on Regional Max Demands |  | 1.057 |  |  | Max Demand Met(MW) |  | Time | Shortage(MW)
Based on State Max Demands |  | 1.096 |  | Solar hr | 196192 |  | 10:54 | 0
|  |  |  | Non-Solar hr | 195059 |  | 19:27 | 0
Diversity factor = Sum of regional or state maximum demands / All India maximum demand
**Note: All generation MU figures are gross
***Godda (Jharkhand) -> Bangladesh power exchange is through the radial connection (isolated from Indian Grid)
Solar Hours -> 06:00 to 18:00hrs and rest are Non-Solar Hours
*Source: RLDCs for solar connected to ISTS; SLDCs for embedded solar. Limited visibility of embedded solar data.
Executive Director-NLDC

## IR-Line
INTER-REGIONAL EXCHANGES
Import=(+ve) /Export =(-ve) for NET (MU)
[6 empty] | Date of Reporting: |  |  | 16-Sep-2024
Sl No | Voltage Level | Line Details | No. of Circuit | Max Import (MW) | Max Export (MW) | Import (MU) | Export (MU) |  | NET (MU)
Import/Export of ER (With NR)
1 | HVDC | ALIPURDUAR-AGRA | 2 | 0 | 700 | 0 | 17.02 |  | -17.02
2 | HVDC | PUSAULI B/B | - | 0 | 112 | 0 | 2.82 |  | -2.82
3 | 765 kV | GAYA-VARANASI | 2 | 383 | 984 | 0 | 10.8 |  | -10.8
4 | 765 kV | SASARAM-FATEHPUR | 1 | 206 | 340 | 0 | 2.96 |  | -2.96
5 | 765 kV | GAYA-BALIA | 1 | 0 | 750 | 0 | 9.9 |  | -9.9
6 | 400 kV | PUSAULI-VARANASI | 1 | 0 | 157 | 0 | 2.86 |  | -2.86
7 | 400 kV | PUSAULI -ALLAHABAD | 1 | 46 | 30 | 0.1 | 0 |  | 0.1
8 | 400 kV | MUZAFFARPUR-GORAKHPUR | 2 | 0 | 846 | 0 | 12.68 |  | -12.68
9 | 400 kV | PATNA-BALIA | 2 | 0 | 988 | 0 | 15.07 |  | -15.07
10 | 400 kV | NAUBATPUR-BALIA | 2 | 0 | 313 | 0 | 4.5 |  | -4.5
11 | 400 kV | BIHARSHARIFF-BALIA | 2 | 73 | 188 | 0 | 3 |  | -3
12 | 400 kV | MOTIHARI-GORAKHPUR | 2 | 0 | 541 | 0 | 7.97 |  | -7.97
13 | 400 kV | BIHARSHARIFF-VARANASI | 2 | 119 | 364 | 0 | 4.74 |  | -4.74
14 | 220 kV | SAHUPURI-KARAMNASA | 1 | 0 | 83 | 0 | 1.59 |  | -1.59
15 | 132 kV | NAGAR UNTARI-RIHAND | 1 | 0 | 0 | 0.06 | 0 |  | 0.06
16 | 132 kV | GARWAH-RIHAND | 1 | 30 | 0 | 0.23 | 0 |  | 0.23
17 | 132 kV | KARMANASA-SAHUPURI | 1 | 0 | 0 | 0 | 1 |  | -1
18 | 132 kV | KARMANASA-CHANDAULI | 1 | 0 | 0 | 0 | 0 |  | 0
ER-NR | [5 empty] | 0.39 | 96.91 |  | -96.52
Import/Export of ER (With WR)
1 | 765 kV | JHARSUGUDA-DHARAMJAIGARH | 4 | 0 | 1595 | 0 | 15.97 |  | -15.97
2 | 765 kV | NEW RANCHI-DHARAMJAIGARH | 2 | 776 | 1376 | 0 | 0.84 |  | -0.84
3 | 765 kV | JHARSUGUDA-DURG | 2 | 0 | 717 | 0 | 8.99 |  | -8.99
4 | 400 kV | JHARSUGUDA-RAIGARH | 4 | 0 | 751 | 0 | 12.45 |  | -12.45
5 | 400 kV | RANCHI-SIPAT | 2 | 134 | 484 | 0 | 2.83 |  | -2.83
6 | 220 kV | BUDHIPADAR-RAIGARH | 1 | 0 | 120 | 0 | 1.94 |  | -1.94
7 | 220 kV | BUDHIPADAR-KORBA | 2 | 0 | 146 | 0 | 1.83 |  | -1.83
ER-WR | [5 empty] | 0 | 44.85 |  | -44.85
Import/Export of ER (With SR)
1 | HVDC | JEYPORE-GAZUWAKA B/B | 2 | 0 | 729 | 0 | 17.41 |  | -17.41
2 | HVDC | TALCHER-KOLAR BIPOLE | 2 | 0 | 2 | 0 | 0 |  | 0
3 | 765 kV | ANGUL-SRIKAKULAM | 2 | 0 | 2579 | 0 | 40.41 |  | -40.41
4 | 400 kV | TALCHER-I/C | 2 | 1813 | 0 | 37.56 | 0 |  | 37.56
5 | 220 kV | BALIMELA-UPPER-SILERRU | 1 | 0 | 0 | 0 | 0 |  | 0
ER-SR | [5 empty] | 0 | 57.82 |  | -57.82
Import/Export of ER (With NER)
1 | 400 kV | BINAGURI-BONGAIGAON | 2 | 0 | 361 | 0 | 5.73 |  | -5.73
2 | 400 kV | ALIPURDUAR-BONGAIGAON | 2 | 0 | 549 | 0 | 8.35 |  | -8.35
3 | 220 kV | ALIPURDUAR-SALAKATI | 2 | 0 | 132 | 0 | 2.18 |  | -2.18
ER-NER | [5 empty] | 0 | 16.26 |  | -16.26
Import/Export of NER (With NR)
1 | HVDC | BISWANATH CHARIALI-AGRA | 2 | 0 | 503 | 0 | 12.03 |  | -12.03
NER-NR | [5 empty] | 0 | 12.03 |  | -12.03
Import/Export of WR (With NR)
1 | HVDC | CHAMPA-KURUKSHETRA | 2 | 0 | 4546 | 0 | 78.98 |  | -78.98
2 | HVDC | VINDHYACHAL B/B | - | 0 | 401 | 0 | 2.47 |  | -2.47
3 | HVDC | MUNDRA-MOHINDERGARH | 2 | 0 | 1448 | 0 | 34.61 |  | -34.61
4 | 765 kV | GWALIOR-AGRA | 2 | 532 | 1368 | 1.26 | 8.51 |  | -7.25
5 | 765 kV | GWALIOR-PHAGI | 2 | 1352 | 1721 | 7.54 | 14.3 |  | -6.76
6 | 765 kV | JABALPUR-ORAI | 2 | 172 | 892 | 0 | 10.37 |  | -10.37
7 | 765 kV | GWALIOR-ORAI | 1 | 800 | 145 | 9.62 | 0.41 |  | 9.21
8 | 765 kV | SATNA-ORAI | 1 | 0 | 707 | 0 | 9.72 |  | -9.72
9 | 765 kV | BANASKANTHA-CHITORGARH | 2 | 1531 | 0 | 25.52 | 0 |  | 25.52
10 | 765 kV | VINDHYACHAL-VARANASI | 2 | 748 | 1761 | 0 | 23.18 |  | -23.18
11 | 400 kV | ZERDA-KANKROLI | 1 | 311 | 0 | 5.3 | 0 |  | 5.3
12 | 400 kV | ZERDA -BHINMAL | 1 | 84 | 75 | 0.53 | 0.32 |  | 0.21
13 | 400 kV | VINDHYACHAL -RIHAND | 1 | 0 | 2 | 0 | 0 |  | 0
14 | 400 kV | RAPP-SHUJALPUR | 2 | 587 | 428 | 4.73 | 1.92 |  | 2.81
15 | 400 kV | NEEMUCH-Chittorgarh | 2 | 518 | 514 | 2.85 | 3.08 |  | -0.23
16 | 220 kV | BHANPURA-RANPUR | 1 | 0 | 81 | 0 | 1.4 |  | -1.4
17 | 220 kV | BHANPURA-MORAK | 1 | 0 | 30 | 0 | 1.61 |  | -1.61
18 | 220 kV | MEHGAON-AURAIYA | 1 | 113 | 3 | 1.01 | 0 |  | 1.01
19 | 220 kV | MALANPUR-AURAIYA | 1 | 87 | 20 | 0.61 | 0.02 |  | 0.59
20 | 132 kV | GWALIOR-SAWAI MADHOPUR | 1 | 0 | 0 | 0 | 0 |  | 0
21 | 132 kV | RAJGHAT-LALITPUR | 2 | 0 | 0 | 0 | 0 |  | 0
WR-NR | [5 empty] | 58.97 | 190.9 |  | -131.93
Import/Export of WR (With SR)
1 | HVDC | BHADRAWATI B/B | - | 0 | 1003 | 21.5 | 0 |  | 21.5
2 | HVDC | RAIGARH-PUGALUR | 2 | 0 | 2506 | 0 | 41.52 |  | -41.52
3 | 765 kV | SOLAPUR-RAICHUR | 2 | 1630 | 1219 | 15.52 | 5.8 |  | 9.72
4 | 765 kV | WARDHA-NIZAMABAD | 2 | 216 | 2432 | 0.24 | 27.14 |  | -26.9
5 | 765 kV | WARORA-WARANGAL(NEW) | 2 | 141 | 2418 | 0.08 | 25.64 |  | -25.56
6 | 400 kV | KOLHAPUR-KUDGI | 2 | 1656 | 0 | 25.97 | 0 |  | 25.97
7 | 220 kV | KOLHAPUR-CHIKODI | 2 | 0 | 0 | 0 | 0 |  | 0
8 | 220 kV | PONDA-AMBEWADI | 1 | 95 | 0 | 1.16 | 0 |  | 1.16
9 | 220 kV | XELDEM-AMBEWADI | 1 | 2 | 109 | 1.98 | 0 |  | 1.98
WR-SR | [5 empty] | 66.45 | 100.1 |  | -33.65
INTERNATIONAL EXCHANGES | [7 empty] | Import(+ve)/Export(-ve)
State |  | Region | Line Name |  | Max (MW) | Min (MW) | Avg (MW) |  | Energy Exchange (MU)
|  | ER | 400kV MANGDECHHU-ALIPURDUAR 1,2&3 i.e. ALIPURDUAR RECEIPT (from MANGDECHU HEP 4*180MW) |  | 767.377 | 721.119 | 749.78 |  | 17.9946
|  | ER | 400kV TALA-BINAGURI 1,2,4 (& 400kV MALBASE - BINAGURI) i.e. BINAGURI RECEIPT (from TALA HEP 6*170MW) |  | 889.459 | 818.989 | 858.13 |  | 20.595
BHUTAN |  | ER | 220kV CHUKHA-BIRPARA 1&2 (& 220kV MALBASE - BIRPARA) i.e. BIRPARA RECEIPT (from CHUKHA HEP 4*84MW) |  | 105.702 | 65.338 | 83.19 |  | 1.9965
|  | NER | 132kV GELEPHU-SALAKATI |  | 33.93 | 22.37 | 27.958 |  | 0.671
|  | NER | 132kV MOTANGA-RANGIA |  | 71.66 | 47.06 | 58.292 |  | 1.399
|  | NR | NEPAL IMPORT (FROM UP) |  | -46 | 0 | 0 |  | 0
NEPAL |  | NR | 132kV MAHENDRANAGAR-TANAKPUR(NHPC) |  | 69.336 | 0 | 49 |  | 1.17
|  | ER | NEPAL IMPORT (FROM BIHAR) |  | 54.32 | 19.66 | 37.5 |  | 0.9
|  | ER | 400kV DHALKEBAR-MUZAFFARPUR 1&2 |  | 721 | 480 | 630.833 |  | 15.14
|  | ER | BHERAMARA B/B HVDC (B'DESH) |  | -927 | -478 | -647.21 |  | -15.533
BANGLADESH |  | ER (Isolated from Indian Grid) | 400kV GODDA_TPS-RAHANPUR (B'DESH) D/C |  | -1131.32 | -811.08 | -908.333 |  | -21.8
|  | NER | 132kV COMILLA-SURAJMANI NAGAR 1&2 |  | -56 | 0 | -47.5 |  | -1.14

## CrossBorder
|  | CROSS BORDER EXCHANGE SCHEDULE | [5 empty] | Date of Reporting: |  |  | 16-Sep-2024
Export From India (in MU)
T-GNA
| GNA |  |  | COLLECTIVE
Country | (ISGS/PPA) |  | BILATERAL | IDAM |  |  | RTM |  |  |  |  | TOTAL
|  |  | TOTAL | IEX | PXIL | HPX | IEX |  | PXIL | HPX
Bhutan | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0
Nepal | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0
Bangladesh | 15.72 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 15.72
Myanmar | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0
Total Export | 15.72 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 15.72
Import by India(in MU)
T-GNA
| GNA |  |  | COLLECTIVE
Country | (ISGA/PPA) |  | BILATERAL | IDAM |  |  | RTM |  |  |  |  | TOTAL
|  |  | TOTAL | IEX | PXIL | HPX | IEX |  | PXIL | HPX
Bhutan | 40.7 |  | 0 | 1.39 | 0 | 0 | 0.07 |  | 0 | 0 |  | 42.16
Nepal | 7.07 |  | 0 | 9.01 | 0 | 0 | 0.22 |  | 0 | 0 |  | 16.3
Bangladesh | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0
Myanmar | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0
Total Import | 47.77 |  | 0 | 10.4 | 0 | 0 | 0.29 |  | 0 | 0 |  | 58.46
Net from India(in MU) -ve : Export / +ve : Import
T-GNA
| GNA |  |  | COLLECTIVE
Country | (ISGS/PPA) |  | BILATERAL | IDAM |  |  | RTM |  |  |  |  | TOTAL
|  |  | TOTAL | IEX | PXIL | HPX | IEX |  | PXIL | HPX
Bhutan | 40.7 |  | 0 | 1.39 | 0 | 0 | 0.07 |  | 0 | 0 |  | 42.16
Nepal | 7.07 |  | 0 | 9.01 | 0 | 0 | 0.22 |  | 0 | 0 |  | 16.3
Bangladesh | -15.72 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | -15.72
Myanmar | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0
Total Net | 32.05 |  | 0 | 10.4 | 0 | 0 | 0.29 |  | 0 | 0 |  | 42.74