## MOP_E
Report for previous day | [5 empty] | Date of Reporting: |  | 12-Mar-2024
A. Power Supply Position at All India and Regional level
|  | NR | WR | SR | ER | NER | TOTAL
Demand Met during Evening Peak hrs(MW) (at 19:00 hrs; from RLDCs) |  | 52689 | 64341 | 52377 | 23392 | 2716 | 195515
Peak Shortage (MW) |  | 330 | 261 | 0 | 248 | 0 | 839
Energy Met (MU) |  | 1102 | 1503.9 | 1363.32 | 498.24 | 48 | 4515.46
Hydro Gen (MU) |  | 124.09 | 40.97 | 56 | 17.59 | 10 | 248.65
Wind Gen (MU) |  | 10.4 | 67.91 | 43.11 | - | - | 121.42
Solar Gen (MU)* |  | 159.12 | 85 | 125.43 | 6.57 | 1.19 | 377.31
Energy Shortage (MU) |  | 0.33 | 0.26 | 0 | 1.597 | 0 | 2.187
Maximum Demand Met During the Day (MW) (From NLDC SCADA) |  | 57825 | 70440 | 67079 | 23837 | 2793 | 217995.487
Time Of Maximum Demand Met |  | 10:14 | 10:32 | 10:54 | 18:31 | 18:15 | 45362.4514
B. Frequency Profile (%)
Region | FVI | < 49.7 | 49.7 - 49.8 | 49.8 - 49.9 | < 49.9 | 49.9 - 50.05 | > 50.05
All India | 0.039 | 0 | 0.36 | 8.11 | 8.47 | 78.35 | 13.18
C. Power Supply Position in States
|  | Max.Demand | Shortage during | Energy Met | Drawal | OD(+)/UD(-) | Max OD | Energy
Region | States | Met during the day (MW) | maximum Demand (MW) | (MU) | Schedule (MU) | (MU) | (MW) | Shortage (MU)
| Punjab | 8164 | 0 | 147.4 | 61.83 | 1.09 | 252 | 0
| Haryana | 7200 | 0 | 140.81 | 106.67 | -0.63 | 217 | 0
| Rajasthan | 15744 | 0 | 294.29 | 84.36 | -1 | 326 | 0
| Delhi | 3908 | 0 | 69.28 | 62.5 | 1.2 | 399 | 0
NR | UP | 17511 | 0 | 316.93 | 55.41 | 0.02 | 471 | 0
| Uttarakhand | 2162 | 0 | 39.28 | 24.88 | 0.94 | 271 | 0
| HP | 1827 | 0 | 30.54 | 24.54 | -0.49 | 83 | 0
| J&K(UT) & Ladakh(UT) | 2754 | 0 | 56.74 | 49.75 | 0.02 | 234 | 0.33
| Chandigarh | 220 | 0 | 3.44 | 3.4 | 0.04 | 54 | 0
| Railways_NR ISTS | 177 | 0 | 3.71 | 3.58 | 0.13 | 22 | 0
| Chhattisgarh | 5912 | 0 | 135.4 | 79 | 2.2 | 433 | 0
| Gujarat | 20417 | 0 | 423.2 | 181.7 | -0.7 | 1004 | 0
| MP | 13292 | 0 | 259.2 | 150 | -4.7 | 513 | 0
WR | Maharashtra | 27627 | 0 | 609.9 | 193.9 | -3.1 | 888 | 0.26
| Goa | 734 | 0 | 15 | 11.8 | 2.7 | 26 | 0
| DNHDDPDCL | 1268 | 0 | 28.6 | 28.5 | 0.1 | 70 | 0
| AMNSIL | 904 | 0 | 20.4 | 10.2 | -0.3 | 272 | 0
| BALCO | 521 | 0 | 12.2 | 12.5 | -0.3 | 14 | 0
| Andhra Pradesh | 13036 | 0 | 241.36 | 90.17 | -0.55 | 443 | 0
| Telangana | 15161 | 0 | 300.22 | 182.75 | -1.44 | 975 | 0
SR | Karnataka | 17110 | 0 | 325.54 | 162.55 | -2.48 | 649 | 0
| Kerala | 5031 | 0 | 100.22 | 77.87 | 1.17 | 279 | 0
| Tamil Nadu | 18605 | 0 | 386.6 | 245.11 | -0.59 | 455 | 0
| Puducherry | 417 | 0 | 9.38 | 9.07 | -0.28 | 24 | 0
| Bihar | 4828 | 0 | 93.1 | 80.39 | 0.25 | 259 | 0
| DVC | 3684 | 0 | 70.62 | -42.56 | -0.15 | 903 | 0
| Jharkhand | 1869 | 213 | 34.86 | 23.81 | -1.44 | 267 | 1.597
ER | Odisha | 6000 | 0 | 133.65 | 65.69 | -2.34 | 325 | 0
| West Bengal | 8021 | 0 | 164.12 | 19.72 | -1.26 | 174 | 0
| Sikkim | 108 | 0 | 1.77 | 1.69 | 0.08 | 33 | 0
| Railways_ER ISTS | 10 | 0 | 0.12 | 0.11 | 0.01 | 2 | 0
| Arunachal Pradesh | 156 | 0 | 2.32 | 2.76 | -0.52 | 23 | 0
| Assam | 1634 | 0 | 28.64 | 23.51 | 0.09 | 119 | 0
| Manipur | 207 | 0 | 2.96 | 3.09 | -3.09 | 28 | 0
NER | Meghalaya | 327 | 0 | 4.97 | 5.06 | -5.06 | 43 | 0
| Mizoram | 134 | 0 | 2 | 1.6 | -1.6 | 23 | 0
| Nagaland | 145 | 0 | 2.28 | 2.3 | -2.3 | 50 | 0
| Tripura | 229 | 0 | 3.98 | 3.91 | -3.91 | 104 | 0
D. Transnational Exchanges (MU) - Import(+ve)/Export(-ve)
|  | Bhutan | Nepal | Bangladesh | Godda -> Bangladesh
Actual (MU) |  | -10.309 | -14.319 | -21.927 | -28.48
Day Peak (MW) |  | -568.06 | -643.34 | -943 | -1475
E. Import/Export by Regions (in MU) - Import(+ve)/Export(-ve); OD(+)/UD(-)
|  | NR | WR | SR | ER | NER | TOTAL
Schedule(MU) |  | 84.33 | -266.58 | 309.49 | -133.14 | 5.9 | 0
Actual(MU) |  | 78.36 | -264.81 | 316.504 | -144.13 | 6.93 | -7.146
O/D/U/D(MU) |  | -5.97 | 1.77 | 7.014 | -10.99 | 1.03 | -7.146
F. Generation Outage(MW)
|  | NR | WR | SR | ER | NER | TOTAL | % Share
Central Sector |  | 7332.92 | 8445.6 | 4078 | 3432 | 567.5 | 23856.02 | 47.593
State Sector |  | 7565.5 | 12066.5 | 3756 | 2746.5 | 134.58 | 26269.08 | 52.407
Total |  | 14898.42 | 20512.1 | 7834 | 6178.5 | 702.08 | 50125.1 | 100
G. Sourcewise generation (Gross) (MU)
|  | NR | WR | SR | ER | NER | All India | % Share
Coal |  | 719.99 | 1588.09 | 750.45 | 719.79 | 12.69 | 3791.01 | 77.1784
Lignite |  | 30.07 | 17.27 | 66.65 | 0 | 0 | 113.99 | 2.3206
Hydro |  | 124.09 | 40.97 | 56 | 17.59 | 10 | 246.39 | 5.0161
Nuclear |  | 31.14 | 42.93 | 51.72 | 0 | 0 | 125.79 | 2.5609
Gas, Naptha & Diesel |  | 9.48 | 43.23 | 6.4 | 0 | 24 | 80.35 | 1.6358
RES (Wind, Solar, Biomass & Others) |  | 188.16 | 155.15 | 201.64 | 8.34 | 1.19 | 554.48 | 11.2883
Total |  | 1102.93 | 1887.64 | 1132.86 | 745.72 | 48 | 4917 | 100
Share of RES in total generation (%) |  | 17.0456 | 8.2162 | 17.7772 | 1.1186 | 2.7144 | 11.2794
Share of Non-fossil fuel (Hydro,Nuclear and RES) in total generation(%) |  | 31.1924 | 12.6963 | 27.3976 | 3.4565 | 24.07 | 18.9287
H. All India Demand Diversity Factor |  |  |  | I. All India Peak Demand and shortage at Solar and Non-Solar Hour
Based on Regional Max Demands |  | 1.018 |  |  | Max Demand Met(MW) |  | Time | Shortage(MW)
Based on State Max Demands |  | 1.041 |  | Solar hr | 217995 |  | 10:50 | 0
|  |  |  | Non-Solar hr | 198401 |  | 19:09 | 839
Diversity factor = Sum of regional or state maximum demands / All India maximum demand
**Note: All generation MU figures are gross
***Godda (Jharkhand) -> Bangladesh power exchange is through the radial connection (isolated from Indian Grid)
Solar Hours -> 07:00 to 17:00hrs and rest are Non-Solar Hours
*Source: RLDCs for solar connected to ISTS; SLDCs for embedded solar. Limited visibility of embedded solar data.
Executive Director-NLDC

## IR-Line
INTER-REGIONAL EXCHANGES
Import=(+ve) /Export =(-ve) for NET (MU)
[6 empty] | Date of Reporting: |  |  | 12-Mar-2024
Sl No | Voltage Level | Line Details | No. of Circuit | Max Import (MW) | Max Export (MW) | Import (MU) | Export (MU) |  | NET (MU)
Import/Export of ER (With NR)
1 | HVDC | ALIPURDUAR-AGRA | 2 | 0 | 0 | 0 | 0 |  | 0
2 | HVDC | PUSAULI B/B | - | 0 | 48 | 0 | 1.27 |  | -1.27
3 | 765 kV | GAYA-VARANASI | 2 | 0 | 748 | 0 | 10.7 |  | -10.7
4 | 765 kV | SASARAM-FATEHPUR | 1 | 0 | 461 | 0 | 7.96 |  | -7.96
5 | 765 kV | GAYA-BALIA | 1 | 0 | 480 | 0 | 6.03 |  | -6.03
6 | 400 kV | PUSAULI-VARANASI | 1 | 17 | 70 | 0 | 0.73 |  | -0.73
7 | 400 kV | PUSAULI -ALLAHABAD | 1 | 24 | 66 | 0 | 0.52 |  | -0.52
8 | 400 kV | MUZAFFARPUR-GORAKHPUR | 2 | 197 | 553 | 0 | 3.74 |  | -3.74
9 | 400 kV | PATNA-BALIA | 2 | 0 | 560 | 0 | 13.1 |  | -13.1
10 | 400 kV | NAUBATPUR-BALIA | 2 | 0 | 514 | 0 | 4.31 |  | -4.31
11 | 400 kV | BIHARSHARIFF-BALIA | 2 | 240 | 102 | 1.58 | 0 |  | 1.58
12 | 400 kV | MOTIHARI-GORAKHPUR | 2 | 8 | 372 | 0 | 5.17 |  | -5.17
13 | 400 kV | BIHARSHARIFF-VARANASI | 2 | 11 | 317 | 0 | 3.58 |  | -3.58
14 | 220 kV | SAHUPURI-KARAMNASA | 1 | 22 | 60 | 0 | 0.28 |  | -0.28
15 | 132 kV | NAGAR UNTARI-RIHAND | 1 | 0 | 0 | 0 | 0 |  | 0
16 | 132 kV | GARWAH-RIHAND | 1 | 30 | 0 | 0 | 0 |  | 0
17 | 132 kV | KARMANASA-SAHUPURI | 1 | 0 | 0 | 0 | 0 |  | 0
18 | 132 kV | KARMANASA-CHANDAULI | 1 | 0 | 0 | 0 | 0 |  | 0
ER-NR | [5 empty] | 1.58 | 57.39 |  | -55.81
Import/Export of ER (With WR)
1 | 765 kV | JHARSUGUDA-DHARAMJAIGARH | 4 | 1603 | 0 | 23.91 | 0 |  | 23.91
2 | 765 kV | NEW RANCHI-DHARAMJAIGARH | 2 | 0 | 1225 | 0 | 19.11 |  | -19.11
3 | 765 kV | JHARSUGUDA-DURG | 2 | 0 | 955 | 0 | 11.9 |  | -11.9
4 | 400 kV | JHARSUGUDA-RAIGARH | 4 | 0 | 540 | 0 | 8.81 |  | -8.81
5 | 400 kV | RANCHI-SIPAT | 2 | 0 | 452 | 0 | 6.8 |  | -6.8
6 | 220 kV | BUDHIPADAR-RAIGARH | 1 | 0 | 154 | 0 | 2.6 |  | -2.6
7 | 220 kV | BUDHIPADAR-KORBA | 2 | 109 | 45 | 0.62 | 0 |  | 0.62
ER-WR | [5 empty] | 24.53 | 49.22 |  | -24.69
Import/Export of ER (With SR)
1 | HVDC | JEYPORE-GAZUWAKA B/B | 2 | 0 | 638 | 0 | 14.57 |  | -14.57
2 | HVDC | TALCHER-KOLAR BIPOLE | 2 | 0 | 1978 | 0 | 40.06 |  | -40.06
3 | 765 kV | ANGUL-SRIKAKULAM | 2 | 0 | 2920 | 0 | 58.78 |  | -58.78
4 | 400 kV | TALCHER-I/C | 2 | 406 | 211 | 4.55 | 0 |  | 4.55
5 | 220 kV | BALIMELA-UPPER-SILERRU | 1 | 0 | 0 | 0 | 0 |  | 0
ER-SR | [5 empty] | 0 | 113.41 |  | -113.41
Import/Export of ER (With NER)
1 | 400 kV | BINAGURI-BONGAIGAON | 2 | 0 | 7 | 0.48 | 0.24 |  | 0.24
2 | 400 kV | ALIPURDUAR-BONGAIGAON | 2 | 411 | 0 | 3.81 | 0 |  | 3.81
3 | 220 kV | ALIPURDUAR-SALAKATI | 2 | 25 | 25 | 0.02 | 0 |  | 0.02
ER-NER | [5 empty] | 4.31 | 0.24 |  | 4.07
Import/Export of NER (With NR)
1 | HVDC | BISWANATH CHARIALI-AGRA | 2 | 466 | 0 | 11.08 | 0 |  | 11.08
NER-NR | [5 empty] | 11.08 | 0 |  | 11.08
Import/Export of WR (With NR)
1 | HVDC | CHAMPA-KURUKSHETRA | 2 | 0 | 990 | 0 | 24.01 |  | -24.01
2 | HVDC | VINDHYACHAL B/B | - | 428 | 0 | 12.16 | 0 |  | 12.16
3 | HVDC | MUNDRA-MOHINDERGARH | 2 | 0 | 980 | 0 | 16.67 |  | -16.67
4 | 765 kV | GWALIOR-AGRA | 2 | 219 | 1617 | 0.2 | 11.99 |  | -11.79
5 | 765 kV | GWALIOR-PHAGI | 2 | 655 | 1488 | 2.13 | 16.87 |  | -14.74
6 | 765 kV | JABALPUR-ORAI | 2 | 270 | 904 | 0 | 6.37 |  | -6.37
7 | 765 kV | GWALIOR-ORAI | 1 | 758 | 0 | 11.92 | 0 |  | 11.92
8 | 765 kV | SATNA-ORAI | 1 | 0 | 1163 | 0 | 19.41 |  | -19.41
9 | 765 kV | BANASKANTHA-CHITORGARH | 2 | 1478 | 98 | 17.29 | 0.02 |  | 17.27
10 | 765 kV | VINDHYACHAL-VARANASI | 2 | 0 | 1879 | 0 | 21.84 |  | -21.84
11 | 400 kV | ZERDA-KANKROLI | 1 | 340 | 0 | 4 | 0 |  | 4
12 | 400 kV | ZERDA -BHINMAL | 1 | 340 | 0 | 3.89 | 0 |  | 3.89
13 | 400 kV | VINDHYACHAL -RIHAND | 1 | 969 | 0 | 21.84 | 0 |  | 21.84
14 | 400 kV | RAPP-SHUJALPUR | 2 | 723 | 271 | 7.22 | 0.53 |  | 6.69
15 | 220 kV | BHANPURA-RANPUR | 1 | 0 | 128 | 0 | 2.17 |  | -2.17
16 | 220 kV | BHANPURA-MORAK | 1 | 0 | 30 | 0 | 1.38 |  | -1.38
17 | 220 kV | MEHGAON-AURAIYA | 1 | 107 | 0 | 1.74 | 0 |  | 1.74
18 | 220 kV | MALANPUR-AURAIYA | 1 | 75 | 0 | 1.06 | 0 |  | 1.06
19 | 132 kV | GWALIOR-SAWAI MADHOPUR | 1 | 0 | 0 | 0 | 0 |  | 0
20 | 132 kV | RAJGHAT-LALITPUR | 2 | 0 | 0 | 0 | 0 |  | 0
WR-NR | [5 empty] | 83.45 | 121.26 |  | -37.81
Import/Export of WR (With SR)
1 | HVDC | BHADRAWATI B/B | - | 0 | 1013 | 0 | 20.32 |  | -20.32
2 | HVDC | RAIGARH-PUGALUR | 2 | 0 | 6531 | 0 | 101.28 |  | -101.28
3 | 765 kV | SOLAPUR-RAICHUR | 2 | 0 | 2114 | 0 | 29.82 |  | -29.82
4 | 765 kV | WARDHA-NIZAMABAD | 2 | 0 | 3064 | 0 | 54.58 |  | -54.58
5 | 765 kV | WARORA-WARANGAL(NEW) | 2 | 0 | 3062 | 0 | 57.72 |  | -57.72
6 | 400 kV | KOLHAPUR-KUDGI | 2 | 969 | 0 | 10.72 | 0 |  | 10.72
7 | 220 kV | KOLHAPUR-CHIKODI | 2 | 0 | 0 | 0 | 0 |  | 0
8 | 220 kV | PONDA-AMBEWADI | 1 | 0 | 0 | 0 | 0 |  | 0
9 | 220 kV | XELDEM-AMBEWADI | 1 | 0 | 123 | 2.32 | 0 |  | 2.32
WR-SR | [5 empty] | 13.04 | 263.72 |  | -250.68
INTERNATIONAL EXCHANGES | [7 empty] | Import(+ve)/Export(-ve)
State |  | Region | Line Name |  | Max (MW) | Min (MW) | Avg (MW) |  | Energy Exchange (MU)
|  | ER | 400kV MANGDECHHU-ALIPURDUAR 1,2&3 i.e. ALIPURDUAR RECEIPT (from MANGDECHU HEP 4*180MW) |  | -212.528 | 104.786 | -108.73 |  | -2.6095
|  | ER | 400kV TALA-BINAGURI 1,2,4 (& 400kV MALBASE - BINAGURI) i.e. BINAGURI RECEIPT (from TALA HEP 6*170MW) |  | -259.814 | 117.729 | -136.46 |  | -3.275
BHUTAN |  | ER | 220kV CHUKHA-BIRPARA 1&2 (& 220kV MALBASE - BIRPARA) i.e. BIRPARA RECEIPT (from CHUKHA HEP 4*84MW) |  | -245.163 | -110.133 | -191.46 |  | -4.595
|  | NER | 132kV GELEPHU-SALAKATI |  | -17.17 | -0.16 | -7.875 |  | -0.189
|  | NER | 132kV MOTANGA-RANGIA |  | 27.11 | -0.4 | 15 |  | 0.36
|  | NR | NEPAL IMPORT (FROM UP) |  | -72 | 0 | -65 |  | -1.55
NEPAL |  | NR | 132kV MAHENDRANAGAR-TANAKPUR(NHPC) |  | -72 | 0 | -56 |  | -1.35
|  | ER | NEPAL IMPORT (FROM BIHAR) |  | -164.34 | 0 | -97.458 |  | -2.339
|  | ER | 400kV DHALKEBAR-MUZAFFARPUR 1&2 |  | -479 | 0 | -378.333 |  | -9.08
|  | ER | BHERAMARA B/B HVDC (B'DESH) |  | -943 | -803 | -913.63 |  | -21.927
BANGLADESH |  | ER (Isolated from Indian Grid) | 400kV GODDA_TPS-RAHANPUR (B'DESH) D/C |  | -1475 | -811 | -1186.667 |  | -28.48
|  | NER | 132kV COMILLA-SURAJMANI NAGAR 1&2 |  |  | 0 | 0 |  | 0

## CrossBorder
|  | CROSS BORDER EXCHANGE SCHEDULE | [5 empty] | Date of Reporting: |  |  | 12-Mar-2024
Export From India (in MU)
T-GNA
| GNA |  |  | COLLECTIVE
Country | (ISGS/PPA) |  | BILATERAL | IDAM |  |  | RTM |  |  |  |  | TOTAL
|  |  | TOTAL | IEX | PXIL | HPX | IEX |  | PXIL | HPX
Bhutan | 0 |  | 0 | 11.64 | 0 | 0 | 0 |  | 0 | 0 |  | 11.64
Nepal | 0.27 |  | 0 | 9.35 | 0 | 0 | 0.13 |  | 0 | 0 |  | 9.75
Bangladesh | 21.95 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 21.95
Myanmar | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0
Total Export | 22.22 |  | 0 | 20.99 | 0 | 0 | 0.13 |  | 0 | 0 |  | 43.34
Import by India(in MU)
T-GNA
| GNA |  |  | COLLECTIVE
Country | (ISGA/PPA) |  | BILATERAL | IDAM |  |  | RTM |  |  |  |  | TOTAL
|  |  | TOTAL | IEX | PXIL | HPX | IEX |  | PXIL | HPX
Bhutan | 0.68 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0.68
Nepal | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0
Bangladesh | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0
Myanmar | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0
Total Import | 0.68 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0.68
Net from India(in MU) -ve : Export / +ve : Import
T-GNA
| GNA |  |  | COLLECTIVE
Country | (ISGS/PPA) |  | BILATERAL | IDAM |  |  | RTM |  |  |  |  | TOTAL
|  |  | TOTAL | IEX | PXIL | HPX | IEX |  | PXIL | HPX
Bhutan | 0.68 |  | 0 | -11.64 | 0 | 0 | 0 |  | 0 | 0 |  | -10.96
Nepal | -0.27 |  | 0 | -9.35 | 0 | 0 | -0.13 |  | 0 | 0 |  | -9.75
Bangladesh | -21.95 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | -21.95
Myanmar | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0
Total Net | -21.54 |  | 0 | -20.99 | 0 | 0 | -0.13 |  | 0 | 0 |  | -42.66