## MOP_E
Report for previous day | [5 empty] | Date of Reporting: |  | 26-Mar-2024
A. Power Supply Position at All India and Regional level
|  | NR | WR | SR | ER | NER | TOTAL
Demand Met during Evening Peak hrs(MW) (at 19:00 hrs; from RLDCs) |  | 42042 | 52025 | 49168 | 19689 | 2431 | 165355
Peak Shortage (MW) |  | 0 | 0 | 0 | 0 | 0 | 0
Energy Met (MU) |  | 958 | 1302.5 | 1301.75 | 451.26 | 45.87 | 4059.38
Hydro Gen (MU) |  | 131.07 | 24.68 | 39.4 | 16.24 | 10.95 | 222.34
Wind Gen (MU) |  | 5.96 | 63.35 | 46.56 | - | - | 115.87
Solar Gen (MU)* |  | 142.93 | 84.9 | 133.42 | 3.21 | 1.15 | 365.61
Energy Shortage (MU) |  | 0 | 0 | 0 | 0.13 | 0 | 0.13
Maximum Demand Met During the Day (MW) (From NLDC SCADA) |  | 44156 | 58225 | 62820 | 20592 | 2511 | 182600
Time Of Maximum Demand Met |  | 09:25 | 00:40 | 11:11 | 18:34 | 18:27 | 10:55
B. Frequency Profile (%)
Region | FVI | < 49.7 | 49.7 - 49.8 | 49.8 - 49.9 | < 49.9 | 49.9 - 50.05 | > 50.05
All India | 0.041 | 0 | 0.82 | 5.79 | 6.61 | 81.45 | 11.94
C. Power Supply Position in States
|  | Max.Demand | Shortage during | Energy Met | Drawal | OD(+)/UD(-) | Max OD | Energy
Region | States | Met during the day (MW) | maximum Demand (MW) | (MU) | Schedule (MU) | (MU) | (MW) | Shortage (MU)
| Punjab | 5729 | 0 | 124.85 | 48.7 | -0.56 | 214 | 0
| Haryana | 4772 | 0 | 99.96 | 76.39 | -1.7 | 166 | 0
| Rajasthan | 12295 | 0 | 239.32 | 56.03 | -1.72 | 358 | 0
| Delhi | 2682 | 0 | 55.65 | 47.1 | 0.15 | 137 | 0
NR | UP | 15026 | 0 | 330.17 | 107.74 | -1.07 | 235 | 0
| Uttarakhand | 1380 | 0 | 26.74 | 16.64 | 0.27 | 120 | 0
| HP | 1228 | 0 | 21.75 | 12.84 | -1.25 | 0 | 0
| J&K(UT) & Ladakh(UT) | 2587 | 0 | 52.81 | 44.82 | -1.16 | 137 | 0
| Chandigarh | 153 | 0 | 2.82 | 3.38 | -0.56 | 4 | 0
| Railways_NR ISTS | 192 | 0 | 4.04 | 3.8 | 0.24 | 38 | 0
| Chhattisgarh | 5219 | 0 | 108.2 | 48.9 | -0.9 | 320 | 0
| Gujarat | 15632 | 0 | 328.3 | 169.1 | -3.2 | 592 | 0
| MP | 11720 | 0 | 240.9 | 136.7 | -4.4 | 410 | 0
WR | Maharashtra | 24208 | 0 | 561 | 185.7 | -1.4 | 681 | 0
| Goa | 599 | 0 | 13.7 | 10.7 | 2.6 | 55 | 0
| DNHDDPDCL | 1137 | 0 | 18.5 | 18.6 | -0.1 | 62 | 0
| AMNSIL | 874 | 0 | 19.4 | 9 | 0 | 278 | 0
| BALCO | 522 | 0 | 12.5 | 12.6 | -0.1 | 4 | 0
| Andhra Pradesh | 12274 | 0 | 226.66 | 82.73 | -1.77 | 695 | 0
| Telangana | 13542 | 0 | 272.87 | 160.37 | -1.25 | 585 | 0
SR | Karnataka | 16272 | 0 | 318.14 | 158.27 | -4.81 | 369 | 0
| Kerala | 5115 | 0 | 101.66 | 87.51 | 0.98 | 209 | 0
| Tamil Nadu | 17711 | 0 | 373.54 | 233.94 | -7.54 | 358 | 0
| Puducherry | 380 | 0 | 8.88 | 8.74 | -0.44 | 14 | 0
| Bihar | 4509 | 0 | 87.3 | 81.07 | 0.33 | 381 | 0.13
| DVC | 3074 | 0 | 63.27 | -31.18 | -0.25 | 293 | 0
| Jharkhand | 1539 | 0 | 33.93 | 24.72 | -2.83 | 188 | 0
ER | Odisha | 5246 | 0 | 113.34 | 43 | -0.47 | 277 | 0
| West Bengal | 7361 | 0 | 151.94 | 23.13 | -3.03 | 278 | 0
| Sikkim | 76 | 0 | 1.36 | 1.54 | -0.18 | 22 | 0
| Railways_ER ISTS | 12 | 0 | 0.12 | 0.12 | 0 | 0 | 0
| Arunachal Pradesh | 159 | 0 | 3.43 | 2.92 | 0.38 | 46 | 0
| Assam | 1331 | 0 | 25.29 | 19.15 | -0.16 | 63 | 0
| Manipur | 205 | 0 | 3.08 | 3.16 | -0.08 | 20 | 0
NER | Meghalaya | 321 | 0 | 5.86 | 5.47 | -0.23 | 27 | 0
| Mizoram | 93 | 0 | 1.93 | 1.62 | -0.22 | 6 | 0
| Nagaland | 140 | 0 | 2.38 | 2.33 | -0.03 | 6 | 0
| Tripura | 264 | 0 | 3.9 | 4.02 | 0.41 | 94 | 0
D. Transnational Exchanges (MU) - Import(+ve)/Export(-ve)
|  | Bhutan | Nepal | Bangladesh | Godda -> Bangladesh
Actual (MU) |  | -6.57 | -4.9 | -23.738 | -22.89
Day Peak (MW) |  | -373 | -272 | -1107 | -1026
E. Import/Export by Regions (in MU) - Import(+ve)/Export(-ve); OD(+)/UD(-)
|  | NR | WR | SR | ER | NER | TOTAL
Schedule(MU) |  | 38.41 | -255.42 | 338.01 | -124.36 | 3.36 | 0
Actual(MU) |  | 34.84 | -248.41 | 353.735 | -147.37 | 3.93 | -3.275
O/D/U/D(MU) |  | -3.57 | 7.01 | 15.725 | -23.01 | 0.57 | -3.275
F. Generation Outage(MW)
|  | NR | WR | SR | ER | NER | TOTAL | % Share
Central Sector |  | 5434.25 | 7863.6 | 3768 | 2797 | 226 | 20088.85 | 42.1845
State Sector |  | 8610.5 | 12432.5 | 3563 | 2756.5 | 170 | 27532.5 | 57.8155
Total |  | 14044.75 | 20296.1 | 7331 | 5553.5 | 396 | 47621.35 | 100
G. Sourcewise generation (Gross) (MU)
|  | NR | WR | SR | ER | NER | All India | % Share
Coal |  | 623.45 | 1390.761 | 661.25 | 669.21 | 12.8 | 3357.471 | 75.8271
Lignite |  | 26.64 | 19.99 | 67.16 | 0 | 0 | 113.79 | 2.5699
Hydro |  | 131.07 | 24.68 | 39.4 | 16.24 | 10.95 | 222.34 | 4.9289
Nuclear |  | 30.83 | 58.71 | 51.61 | 0 | 0 | 141.15 | 3.1878
Gas, Naptha & Diesel |  | 9.95 | 24.4 | 5.9 | 0 | 24.36 | 64.61 | 1.4592
RES (Wind, Solar, Biomass & Others) |  | 168.68 | 151.32 | 206.33 | 5.04 | 1.17 | 532.54 | 12.0272
Total |  | 990.62 | 1669.861 | 1031.65 | 690.49 | 49.28 | 4431.901 | 100
Share of RES in total generation (%) |  | 17.0277 | 9.0618 | 20 | 0.72992 | 2.3742 | 12.0161
Share of Non-fossil fuel (Hydro,Nuclear and RES) in total generation(%) |  | 33.371 | 14.0557 | 28.8218 | 3.0819 | 24.5942 | 20.2177
H. All India Demand Diversity Factor |  |  |  | I. All India Peak Demand and shortage at Solar and Non-Solar Hour
Based on Regional Max Demands |  | 1.031 |  |  | Max Demand Met(MW) |  | Time | Shortage(MW)
Based on State Max Demands |  | 1.071 |  | Solar hr | 182600 |  | 10:55 | 0
|  |  |  | Non-Solar hr | 170390 |  | 0:15 | 0
Diversity factor = Sum of regional or state maximum demands / All India maximum demand
**Note: All generation MU figures are gross
***Godda (Jharkhand) -> Bangladesh power exchange is through the radial connection (isolated from Indian Grid)
Solar Hours -> 07:00 to 17:00hrs and rest are Non-Solar Hours
*Source: RLDCs for solar connected to ISTS; SLDCs for embedded solar. Limited visibility of embedded solar data.
Executive Director-NLDC

## IR-Line
INTER-REGIONAL EXCHANGES
Import=(+ve) /Export =(-ve) for NET (MU)
[6 empty] | Date of Reporting: |  |  | 26-Mar-2024
Sl No | Voltage Level | Line Details | No. of Circuit | Max Import (MW) | Max Export (MW) | Import (MU) | Export (MU) |  | NET (MU)
Import/Export of ER (With NR)
1 | HVDC | ALIPURDUAR-AGRA | 2 | 0 | 0 | 0 | 0 |  | 0
2 | HVDC | PUSAULI B/B | - | 0 | 48 | 0 | 1.16 |  | -1.16
3 | 765 kV | GAYA-VARANASI | 2 | 494 | 927 | 0 | 8.56 |  | -8.56
4 | 765 kV | SASARAM-FATEHPUR | 1 | 124 | 446 | 0 | 5.13 |  | -5.13
5 | 765 kV | GAYA-BALIA | 1 | 4 | 542 | 0 | 6.47 |  | -6.47
6 | 400 kV | PUSAULI-VARANASI | 1 | 0 | 93 | 0 | 1.2 |  | -1.2
7 | 400 kV | PUSAULI -ALLAHABAD | 1 | 44 | 43 | 0.04 | 0 |  | 0.04
8 | 400 kV | MUZAFFARPUR-GORAKHPUR | 2 | 251 | 444 | 0 | 2.75 |  | -2.75
9 | 400 kV | PATNA-BALIA | 2 | 15 | 484 | 0 | 9.01 |  | -9.01
10 | 400 kV | NAUBATPUR-BALIA | 2 | 38 | 246 | 0 | 2.64 |  | -2.64
11 | 400 kV | BIHARSHARIFF-BALIA | 2 | 256 | 160 | 1.18 | 0 |  | 1.18
12 | 400 kV | MOTIHARI-GORAKHPUR | 2 | 60 | 388 | 0 | 4.2 |  | -4.2
13 | 400 kV | BIHARSHARIFF-VARANASI | 2 | 217 | 246 | 0 | 0.4 |  | -0.4
14 | 220 kV | SAHUPURI-KARAMNASA | 1 | 16 | 76 | 0 | 0.81 |  | -0.81
15 | 132 kV | NAGAR UNTARI-RIHAND | 1 | 0 | 0 | 0 | 0 |  | 0
16 | 132 kV | GARWAH-RIHAND | 1 | 0 | 0 | 0 | 0 |  | 0
17 | 132 kV | KARMANASA-SAHUPURI | 1 | 0 | 0 | 0 | 0 |  | 0
18 | 132 kV | KARMANASA-CHANDAULI | 1 | 0 | 0 | 0 | 0 |  | 0
ER-NR | [5 empty] | 1.22 | 42.33 |  | -41.11
Import/Export of ER (With WR)
1 | 765 kV | JHARSUGUDA-DHARAMJAIGARH | 4 | 806 | 50 | 8.43 | 0 |  | 8.43
2 | 765 kV | NEW RANCHI-DHARAMJAIGARH | 2 | 0 | 1721 | 0 | 21.95 |  | -21.95
3 | 765 kV | JHARSUGUDA-DURG | 2 | 0 | 1221 | 0 | 23.06 |  | -23.06
4 | 400 kV | JHARSUGUDA-RAIGARH | 4 | 0 | 499 | 0 | 6.34 |  | -6.34
5 | 400 kV | RANCHI-SIPAT | 2 | 0 | 471 | 0 | 5.98 |  | -5.98
6 | 220 kV | BUDHIPADAR-RAIGARH | 1 | 0 | 148 | 0 | 2 |  | -2
7 | 220 kV | BUDHIPADAR-KORBA | 2 | 103 | 0 | 1.21 | 0 |  | 1.21
ER-WR | [5 empty] | 9.64 | 59.33 |  | -49.69
Import/Export of ER (With SR)
1 | HVDC | JEYPORE-GAZUWAKA B/B | 2 | 86 | 745 | 0 | 17.64 |  | -17.64
2 | HVDC | TALCHER-KOLAR BIPOLE | 2 | 0 | 1496 | 0 | 36.11 |  | -36.11
3 | 765 kV | ANGUL-SRIKAKULAM | 2 | 0 | 3018 | 0 | 60.39 |  | -60.39
4 | 400 kV | TALCHER-I/C | 2 | 425 | 490 | 6.92 | 0 |  | 6.92
5 | 220 kV | BALIMELA-UPPER-SILERRU | 1 | 0 | 0 | 0 | 0 |  | 0
ER-SR | [5 empty] | 0 | 114.14 |  | -114.14
Import/Export of ER (With NER)
1 | 400 kV | BINAGURI-BONGAIGAON | 2 | 2 | 6 | 2.5 | 0 |  | 2.5
2 | 400 kV | ALIPURDUAR-BONGAIGAON | 2 | 743 | 0 | 9.33 | 0 |  | 9.33
3 | 220 kV | ALIPURDUAR-SALAKATI | 2 | 108 | 0 | 1.54 | 0 |  | 1.54
ER-NER | [5 empty] | 13.37 | 0 |  | 13.37
Import/Export of NER (With NR)
1 | HVDC | BISWANATH CHARIALI-AGRA | 2 | 660 | 0 | 16.2 | 0 |  | 16.2
NER-NR | [5 empty] | 16.2 | 0 |  | 16.2
Import/Export of WR (With NR)
1 | HVDC | CHAMPA-KURUKSHETRA | 2 | 0 | 2514 | 0 | 58.58 |  | -58.58
2 | HVDC | VINDHYACHAL B/B | - | 257 | 0 | 6.06 | 0 |  | 6.06
3 | HVDC | MUNDRA-MOHINDERGARH | 2 | 0 | 301 | 0 | 7.3 |  | -7.3
4 | 765 kV | GWALIOR-AGRA | 2 | 728 | 1053 | 5.23 | 4.09 |  | 1.14
5 | 765 kV | GWALIOR-PHAGI | 2 | 1377 | 1050 | 5.85 | 11.19 |  | -5.34
6 | 765 kV | JABALPUR-ORAI | 2 | 485 | 403 | 4.3 | 0 |  | 4.3
7 | 765 kV | GWALIOR-ORAI | 1 | 671 | 0 | 10.71 | 0 |  | 10.71
8 | 765 kV | SATNA-ORAI | 1 | 0 | 886 | 0 | 14.93 |  | -14.93
9 | 765 kV | BANASKANTHA-CHITORGARH | 2 | 2016 | 0 | 30.84 | 0 |  | 30.84
10 | 765 kV | VINDHYACHAL-VARANASI | 2 | 111 | 1579 | 0 | 20.66 |  | -20.66
11 | 400 kV | ZERDA-KANKROLI | 1 | 385 | 171 | 6.07 | 0 |  | 6.07
12 | 400 kV | ZERDA -BHINMAL | 1 | 384 | 183 | 6.8 | 0.96 |  | 5.84
13 | 400 kV | VINDHYACHAL -RIHAND | 1 | 967 | 0 | 18.69 | 0 |  | 18.69
14 | 400 kV | RAPP-SHUJALPUR | 2 | 918 | 87 | 9.23 | 0.12 |  | 9.11
15 | 220 kV | BHANPURA-RANPUR | 1 | 0 | 91 | 0 | 1.48 |  | -1.48
16 | 220 kV | BHANPURA-MORAK | 1 | 0 | 30 | 0 | 0.65 |  | -0.65
17 | 220 kV | MEHGAON-AURAIYA | 1 | 111 | 0 | 1.81 | 0 |  | 1.81
18 | 220 kV | MALANPUR-AURAIYA | 1 | 78 | 1 | 1.08 | 0 |  | 1.08
19 | 132 kV | GWALIOR-SAWAI MADHOPUR | 1 | 0 | 0 | 0 | 0 |  | 0
20 | 132 kV | RAJGHAT-LALITPUR | 2 | 0 | 0 | 0 | 0 |  | 0
WR-NR | [5 empty] | 106.67 | 119.96 |  | -13.29
Import/Export of WR (With SR)
1 | HVDC | BHADRAWATI B/B | - | 0 | 1012 | 0 | 23.92 |  | -23.92
2 | HVDC | RAIGARH-PUGALUR | 2 | 0 | 6620 | 0 | 124.6 |  | -124.6
3 | 765 kV | SOLAPUR-RAICHUR | 2 | 0 | 2251 | 0 | 31.16 |  | -31.16
4 | 765 kV | WARDHA-NIZAMABAD | 2 | 0 | 3411 | 0 | 59.19 |  | -59.19
5 | 765 kV | WARORA-WARANGAL(NEW) | 2 | 0 | 3354 | 0 | 58.01 |  | -58.01
6 | 400 kV | KOLHAPUR-KUDGI | 2 | 749 | 87 | 10.34 | 0 |  | 10.34
7 | 220 kV | KOLHAPUR-CHIKODI | 2 | 0 | 0 | 0 | 0 |  | 0
8 | 220 kV | PONDA-AMBEWADI | 1 | 2 | 0 | 0.03 | 0 |  | 0.03
9 | 220 kV | XELDEM-AMBEWADI | 1 | 0 | 101 | 1.64 | 0 |  | 1.64
WR-SR | [5 empty] | 12.01 | 296.88 |  | -284.87
INTERNATIONAL EXCHANGES | [7 empty] | Import(+ve)/Export(-ve)
State |  | Region | Line Name |  | Max (MW) | Min (MW) | Avg (MW) |  | Energy Exchange (MU)
|  | ER | 400kV MANGDECHHU-ALIPURDUAR 1,2&3 i.e. ALIPURDUAR RECEIPT (from MANGDECHU HEP 4*180MW) |  | 184.923 | -100.849 | -4.77 |  | -0.1145
|  | ER | 400kV TALA-BINAGURI 1,2,4 (& 400kV MALBASE - BINAGURI) i.e. BINAGURI RECEIPT (from TALA HEP 6*170MW) |  | 236.812 | -201.626 | -70.92 |  | -1.702
BHUTAN |  | ER | 220kV CHUKHA-BIRPARA 1&2 (& 220kV MALBASE - BIRPARA) i.e. BIRPARA RECEIPT (from CHUKHA HEP 4*84MW) |  | -265.023 | -40.133 | -197.5 |  | -4.74
|  | NER | 132kV GELEPHU-SALAKATI |  | -20.6 | 0 | -11.667 |  | -0.28
|  | NER | 132kV MOTANGA-RANGIA |  | 20.6 | 0 | 11.25 |  | 0.27
|  | NR | NEPAL IMPORT (FROM UP) |  | -50 | 0 | 0 |  | 0
NEPAL |  | NR | 132kV MAHENDRANAGAR-TANAKPUR(NHPC) |  | -50 | 0 | -33 |  | -0.79
|  | ER | NEPAL IMPORT (FROM BIHAR) |  | 0 | 0 | 0 |  | 0
|  | ER | 400kV DHALKEBAR-MUZAFFARPUR 1&2 |  | -272 | -60 | -171.25 |  | -4.11
|  | ER | BHERAMARA B/B HVDC (B'DESH) |  | -947 | -513 | -857.42 |  | -20.578
BANGLADESH |  | ER (Isolated from Indian Grid) | 400kV GODDA_TPS-RAHANPUR (B'DESH) D/C |  | -1026 | -816 | -953.75 |  | -22.89
|  | NER | 132kV COMILLA-SURAJMANI NAGAR 1&2 |  | -160 | 0 | -131.6667 |  | -3.16

## CrossBorder
|  | CROSS BORDER EXCHANGE SCHEDULE | [5 empty] | Date of Reporting: |  |  | 26-Mar-2024
Export From India (in MU)
T-GNA
| GNA |  |  | COLLECTIVE
Country | (ISGS/PPA) |  | BILATERAL | IDAM |  |  | RTM |  |  |  |  | TOTAL
|  |  | TOTAL | IEX | PXIL | HPX | IEX |  | PXIL | HPX
Bhutan | 0 |  | 0 | 7.33 | 0 | 0 | 0.45 |  | 0 | 0 |  | 7.78
Nepal | 0.24 |  | 0 | 4.52 | 0 | 0 | 0.17 |  | 0 | 0 |  | 4.93
Bangladesh | 20.57 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 20.57
Myanmar | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0
Total Export | 20.81 |  | 0 | 11.85 | 0 | 0 | 0.62 |  | 0 | 0 |  | 33.28
Import by India(in MU)
T-GNA
| GNA |  |  | COLLECTIVE
Country | (ISGA/PPA) |  | BILATERAL | IDAM |  |  | RTM |  |  |  |  | TOTAL
|  |  | TOTAL | IEX | PXIL | HPX | IEX |  | PXIL | HPX
Bhutan | 0.48 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0.48
Nepal | 0 |  | 0 | 0 | 0 | 0 | 0.08 |  | 0 | 0 |  | 0.08
Bangladesh | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0
Myanmar | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0
Total Import | 0.48 |  | 0 | 0 | 0 | 0 | 0.08 |  | 0 | 0 |  | 0.56
Net from India(in MU) -ve : Export / +ve : Import
T-GNA
| GNA |  |  | COLLECTIVE
Country | (ISGS/PPA) |  | BILATERAL | IDAM |  |  | RTM |  |  |  |  | TOTAL
|  |  | TOTAL | IEX | PXIL | HPX | IEX |  | PXIL | HPX
Bhutan | 0.48 |  | 0 | -7.33 | 0 | 0 | -0.45 |  | 0 | 0 |  | -7.3
Nepal | -0.24 |  | 0 | -4.52 | 0 | 0 | -0.09 |  | 0 | 0 |  | -4.85
Bangladesh | -20.57 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | -20.57
Myanmar | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0
Total Net | -20.33 |  | 0 | -11.85 | 0 | 0 | -0.54 |  | 0 | 0 |  | -32.72